## Slide 1
Water Loss Audits Using the AWWA M36 Software – Creating and Implementing an Audit for Your System
Peter Nathanson
peternathanson2018@gmail.com
Notes: 1

## Slide 2
What we will learn
2
What is a Water Audit?
What are the Benefits to annual water audits?
What triggers voluntary & required water audits?
How to conduct a water audit using AWWA M36 software
How to interpret and report data validity
How to interpret audit results – Volumes and Values
How to interpret results from AWWA M36 software
How to use results to implement corrective actions

## Slide 3
Acknowledgements
3
Majority of original content developed by Cavanaugh & Associates and SWEFC under contract to NMED-DWB
Further content added by DWB Technical Services staff:
  Michael Peterson
  Peter Nathanson
  Brian Barrick
  Martin Torres

## Slide 4
Old Terminology – no longer used
4
Unaccounted For Water
  Fails to segregate water loss into its components for effective management
  Unreliable indicator of performance
Unaccounted for Water Percentage
  <10 % acceptable
  10-15% needs attention
  > 15% needs immediate attention

## Slide 5
Unaccounted for Water Percentage
5

## Slide 6
Unaccounted for Water Percentage
6

## Slide 7
What is the Water Balance?
7
In this section you will learn to:
1) Utilize the Water Balance
2) Separate Total Water Loss into Real and Apparent Loss
3) Separate Real and Apparent Loss into their sub-components
4) Use metrics in units of Volume, Value, & Validity

## Slide 8
AWWA Water Balance
8

## Slide 9
Billed Water Exported
9
Water exported to consecutive connection systems sold at a wholesale rate
Required data:
  Volume (annual & monthly)
  Revenue (annual & monthly)
Data issues:
  Metered or estimated water consumption?
  Metering inaccuracies
  Data transcription

## Slide 10
Billed metered consumption
10
Water sold at retail rate to customers/members of the water system
Required Data:
  Rate Structure
  Volume sold (annual & monthly)
  Revenue (annual & monthly)
Data issues:
  Metered or estimated consumption?
  Meter inaccuracy
  Data transcription

## Slide 11
Billed Unmetered Consumption
11
Flat-rate, non-metered customer (Construction contracts, Fire Department)
Required data:
  Estimated volume consumed (annual & monthly)
  Revenue (annual & monthly)
Data issues:
  No meters
  Estimated volumes

## Slide 12
Unbilled Metered Consumption
12
Water that is delivered to customers who don’t pay, but volume consumed is recorded
Required Data
  Usage (annual & monthly)
  Fire Department usage, if Fire Department uses meters during training & suppression (annual & monthly)
Data issues
  Meter inaccuracy

## Slide 13
AWWA Water Balance
13
Real
Losses
Apparent
Losses
Unbilled
Authorized
Consumption
Billed
Authorized
Consumption
Non-
Revenue
Water
Revenue
Water
Leakage & Overflows at Storage
Billed Unmetered Consumption
Billed Metered Consumption
Billed Water Exported
Leakage on Service Lines
Leakage on Mains
Systematic Data Handling Errors
Customer Metering Inaccuracies
Unauthorized Consumption
Unbilled Unmetered Consumption
Unbilled Metered Consumption
Water
Imported
Own
Sources
Total
System
Input
( allow
for
known
errors )
Water
Losses
Authorized
Consumption
Water
Exported
Water
Supplied

## Slide 14
AWWA Water Balance
14
Real
Losses
Apparent
Losses
Unbilled
Authorized
Consumption
Non-
Revenue
Water

## Slide 15
Non-Revenue Water
15
Unbilled Authorized:
  Fire Department
  Operational Flushing
Apparent Losses:
  Non-physical/revenue loss
  Meter inaccuracy, billing issues, theft
Real Losses:
  Physical losses
  Leaks, Storage overflow
Real
Losses
Apparent
Losses
Unbilled
Authorized
Consumption
Non-
Revenue
Water

## Slide 16
Apparent Losses - Unbilled unmetered Consumption
16
Water delivered to customers that do not pay for water service; Fire suppression
Required Data:
  Estimates of volume used for fire services (annual & monthly)
  Estimates of volume supplied to customers (annual & monthly)
  Operational Flushing volumes if not metered (annual & monthly)
Data issues:
  Estimates, not known data

## Slide 17
Apparent Losses - Unauthorized Consumption
17
Includes water that is taken against the policies of the water utility (Illegal connections, open bypasses, misuse of fire hydrants, theft)
Required data:
  Examine occurrences of unauthorized consumption, obtain quantities.
Data issues:
  Estimates
  Poor records for basis of estimating

## Slide 18
Apparent Losses - Customer metering & data inaccuracies
18
Customer meter considerations
  Meter age?
  Testing/calibration policy?
  Replacement policy?
  Is the meter the right meter for the job?
Required Data
  Average customer meter inaccuracy (%), weighted by meter size if available (annual)\
Data issues
  Data trancription

## Slide 19
Real Losses - Leakage on Mains
19
Leakage at joints or along pipe sections of distribution main
Required data:
  Estimates of
leakage
Data Issues
  Estimates, data
transcription

## Slide 20
Real Losses - Leakage along service lines
20
Leakage along service connection lines
Data requirements:
  Estimated average loss on service connection between distribution main and customer meter, multiplied by amount of connections
  Average length of service line
Data issues:
  Estimation
  Data not routinely collected

## Slide 21
Real Losses - Leakage & overflow at storage
21
Leakage from storage facilities due to:
  Overflow (check SCADA/pressure switches to control pump)
  Inadequate facility walls
  Inadequate facility foundation
Data requirements:
  Estimated volume lost from storage leakage (annual)
Data issues:
  Estimates
  Data not routinely collected

## Slide 22
Meter Inaccuracy
22

## Slide 23
Meter Inaccuracy
23
8” Propeller Meter
Check Valve
Well Pump
Accuracy results from MFR test bench: 99.5%
Accuracy results from in-situ test: 142.2%
Courtesy MESCO

## Slide 24
Benefits of completing annual audits
24
Increased knowledge of water system
Metric to determine areas to focus to improve overall system performance
Improved future asset and maintenance project planning
Streamline billing & operations

## Slide 25
Why should our PWS do a Water Loss Audit? 1
25
Water Resources Management Concerns
  Only water needed for usage is withdrawn
  Limit need for additional water resources
  Ease water restrictions
  Serve additional customers without expanding source
Financial Concerns
  Recover revenue from customers that have been underpaying, or not paying
  Reduce operational costs for pumping, chemical treatment and maintenance
  Reduce liability

## Slide 26
Why should our PWS do a Water Loss Audit? 2
26
Operational Concerns
  Increased knowledge of distribution system
  Basis for optimized operations
  Safeguard public health and safety
  Improved public relations
  Reduced disruption to customers
System Integrity
  Improved data integrity
  Review of customer billing practices and procedures
  Prevention of contamination

## Slide 27
Voluntary Triggers
27
PWS suspects major water loss and:
  Wants to physically look for leaks (post-holing)
  Wants to request public funding for distribution system rehabilitation
DWB/SWEFC can provide assistance completing water audit

## Slide 28
Required Triggers
28
DWB
  Enforcement, Case-by-case basis
NMOSE
  Water Conservation Planning Guide for Public Water Suppliers

## Slide 29
How to Conduct Audit using AWWA M36 software
29

## Slide 30
What information do we need to complete a water audit? (1 of 4)
30
Master/Source Meter volumes (annual & monthly)
  Include master meters for bulk purchase or wholesale
Customer meter data (annual & monthly)
  Volume of water sold @ retail rate
  Volume of water sold @ wholesale rate
List of unbilled customers (metered & non-metered), Number of active & inactive service connections

## Slide 31
What information do we need to complete a water audit? (2 of 4)
31
Rate Structure
  Volume of water sold @ retail rate
  Volume of water sold @ wholesale rate
Total annual cost of operating water system (salaries, vehicles, maintenance, power, chemicals, etc.)
Total annual cost for power and chemicals for water production/purification/disinfection
Total length of distribution mains

## Slide 32
32
Occurrence of leaks (annual & monthly)
Source/Master Meter info:
  Age
  Date of last calibration
  Calibration records if available
Customer Meter info:
  Average age
  Testing/replacement policy
What information do we need to complete a water audit? (3 of 4)

## Slide 33
What information do we need to complete a water audit? (4 of 4)
33
Policies/Procedures for:
  Source meters
  Customer meters,
  Meter replacement policy
  Operational policies
  Financial & recordkeeping
Normal practices relating to flushing for operators, fire hydrant flushing, fire suppression logs.

## Slide 34
AWWA Free Water Loss Audit Software
34
Standard Data Collection tool in North America
Inputs
  13 volume inputs
  5 system attribute inputs
  3 cost inputs
After Default or n/a’s
  10-12 inputs to actually deal with
https://www.awwa.org/home/awwa-news-details/articleid/2641/awwa-free-water-audit-software-version-5-0-now-available.aspx

## Slide 35
Develop the inputs
35
Develop the input
  Trace from production reports
  Trace from meter testing reports
Data Validity
  Look for missing/extra volumes
  Mismatched timeframe
  Error adjustment should be weighted average

## Slide 36
Develop the inputs
36
Data from:
  Billing reports
  Flushing tracker
  Fire department tracker
Data validity Issues
  Billing report inaccuracies
  Double counting Water Exported in Billed Metered
  Double counting Unbilled Metered consumption in Billed Metered Consumption
  Including leaks/breaks in Unbilled Unmetered

## Slide 37
Develop the inputs
37
Data from:
  Billing/usage reports
  Customer Meter calibration records
  Approximate from meter system, age/condition
Data Validity Issues
  Customer meter calibration not always known, estimates

## Slide 38
Develop the inputs
38
Data from:
  System maps
  Billing system/ database
Data Validity Issues
  Include hydrant leads in Length of Mains
  Include inactive connections
  Billing system reports customers, not connections

## Slide 39
Develop the Inputs
39
Data from:
  Operating budget
  Rate structure
Typical Ranges:
  $2-$10/kgal for CRUC
  $200 - $1000/MG for VPC (systems producing water)
Data Validity Issues
  Don’t include wastewater costs if associated budget
  Consider sewer rates in customer retail unit cost
  Confusing units for variable production costs

## Slide 40
How to conduct a Water Audit - Activity 1
40
Placeholder for Hands-On Activity #1
  download and run initial water audit using Rockville WSC data
  Follow-up using your own system data

## Slide 41
Data Validity
41

## Slide 42
Data Grade Entry
42
Data Grades

## Slide 43
Data Grade Entry
43
Hover the cursor over the red triangle in the corner

## Slide 44
Data Grade Entry
44
Data Grade criteria will show up in a pop-up box

## Slide 45
Data Grade Entry
45
Note the comment on the water audit spreadsheet.

## Slide 46
Data Grade Selection
46
If you are able to check all the boxes move up.

## Slide 47
Data Grade Selection
47
If you are able to check all the boxes move up.
If you aren’t able to check all the boxes move down.

## Slide 48
Data Grade Selection
48
If you are able to check all the boxes on one number and only some of the boxes on the number two above, choose the “conditions between…” box.

## Slide 49
What is the Right Data Grade?
49
ANY NUMBER AS LONG AS IT ACURATELY REPRESENTS THE TRUE SITUATION

## Slide 50
Data Grade Entry
50
Water Audit Data Validity Score

## Slide 51
If the Data Validity Score is below 50, What Should be the Response?
51
What Response?

## Slide 52
Data Grade Entry
52
Priority Areas for Attention to Increase Validity Score
Note: The data grades do not have equal value in the calculation of validity

## Slide 53
If Data Validity Score is greater than 50, What should be the response?
53
Evaluate the Metrics
20 – 200
400 – 4000
2 – 10
*** YOUR WATER AUDIT DATA VALIDITY SCORE IS: 58 out of 100 ***
>50 (validated
score)
4 - 40

## Slide 54
Check the Metrics
54
Metrics vs. Practices
  Inside the range – are they high, mid, or low?
  How does that compare to water loss management practices?
20 – 200
4 – 40
400 – 4000
2 – 10

## Slide 55
If Data Validity Score is greater than 50, What should be the response?
55
Evaluate the Metrics
20 – 200
400 – 4000
2 – 10
*** YOUR WATER AUDIT DATA VALIDITY SCORE IS: 71 out of 100 ***
>50 (validated
score)
4 - 40

## Slide 56
Data Validity – Activity 2
56
Placeholder for Hands-On Activity #2
  update initial audit from Rockville WSC data validity info
  Check for data validity issues
  Include data validity scoring
Applied Activity #2
  update your system audit with data validity grades
  Note from audit results top 3 priority areas for further investigation needed to improve overall data validity score

## Slide 57
Corrective Actions – Data Validity Score < 50
57
Improve Data validity for next audit cycle
  Install customer meters, or implement calibration policy
  Install or calibrate source meters
  Improve policy on water usage estimates for non-metered users

## Slide 58
Corrective Actions – Data Validity Score > 50
58
Flow Tests on Supply/master meters
Signal calibration
Scrub of production data:
  Data gaps
  Irregular patterns
Scrub billing Data:
  Duplicate volumes
  Non-potable volumes
  Wrong timeframes
  Irregular patterns

## Slide 59
Audit Results - Volumes and Values
59
Software calculates loss of water in Volume and Cost (Non-revenue water)

## Slide 60
Volumes and Values – 3-V concept
60
Validity
Value
Volume
MG per Year
Gal/connection/day
Leakage Index
$ per Year
Economic Loss Index
Water Audit Data Validity Score
95% Confidence Limits
Key Data Input Grades

## Slide 61
Volume
Value
61
Notes: Then at the next level – the 3 main ‘components’ of NRW - - Real Loss, Apparent Loss and Unbilled Consumption
Volumes and Values of each - - this is how you are able to dial in further on where the opportunities lie

## Slide 62
Volume
Value
62
Notes: Then at the next level – subcomponents of each of the 3 NRW components. This is where rubber starts to meet the road.
This is where we begin to see where the real opportunities and priorities lie. In this example – it is Meter Inaccuracy and Unreported Leakage. {point out red and blue bars on $$ chart}

## Slide 63
Volumes and Values – Large System Volume
63
1.5 MG/yr supplied, $3 million/yr total cost to operate water system

## Slide 64
Volumes and Values – Large system Cost
64
System info: 1.5 MG/yr supplied, $3 million/yr total cost to operate water system

## Slide 65
How to interpret results
65

## Slide 66
Corrective Actions – Data validity Scores > 50
66
Improve system performance, identify if Real Loss or Apparent Losses dominate
  Status Component Analysis for Real Loss
  Status Component Analysis for Apparent Loss

## Slide 67
Real Loss Component analysis
Unreported
Reported
Background

## Slide 68
Component Analysis – Real Loss
68
LEAKAGE OR OVERFLOW AT STORAGE TANKS
LEAKAGE ON MAINS
LEAKAGE ON SERVICE LINES

## Slide 69
Real Loss Component Analysis
69
From a formula. Need to provide the ICF.
From your repair records.

## Slide 70
Component Analysis- Real Loss
70
Categories of Water Loss
Unavoidable
Detectable
Observable

## Slide 71
Real Loss Component Analysis: The Life of a Leak; Awareness, Location & Repair
71

## Slide 72
Real Loss Component Analysis: Basic data needed
72
Failure Data
  Break type: reported/unreported
  Main or service
  Location
  Line size
  Day/time break discovered
  Day/time break was repaired
Other Data
  Storage tank volume (total)
  Average age of pipe network
  Data from AWWA M36 water audit

## Slide 73
Real Loss Component Analysis Results
73

## Slide 74
Real Loss Component Analysis Results
74

## Slide 75
Component Analysis – Real Loss
75
What is my quantity of Unavoidable or Background Leakage (UARL)?
  Calculate based on:

## Slide 76
Component Analysis – Real Loss
76
Pressure is a Big Factor
PRESSURE
LOSSES
PRESSURE
LOSSES

## Slide 77
Component Analysis – Real Loss
77
Tools to address Background leakage:
  Pressure stabilization
  Pressure reduction
  Main and service line replacement
  Reduction of # of joints and fittings

## Slide 78
Component Analysis – Real Loss
78
Reported Leaks
  Condition, type, & length of pipe
  Depth
  Type of soil
  Installation
  Pressure
  Inspection of system

## Slide 79
Component Analysis – Real Loss
79
Tools to Address Reported Breaks
  Pressure stabilization
  Pressure reduction
  Main and service replacement
  Optimize repair and response time

## Slide 80
Real Loss Component Analysis – Activity 3
80
Placeholder for Hands-On Activity #3
  Use AWWARf Leakage Component Analysis Model to update initial audit from Rockville WSC
  Identify volume & value of the real loss sub-component of the Rockville WSC NRW
Applied Activity #3
  Assemble and input your system’s break data into the AWWARf model
  Otherwise, develop a plan to collect, assemble and use the required break data for your audit

## Slide 81
Component Analysis – Apparent Losses
81
Create a water balance: separate Non-Revenue Water into Unbilled Consumption, Apparent Loss and Real Loss.
Test the validity: Data Validity Score & Metrics screening, data validity checking
Analyze the components of Unbilled Consumption, Apparent Loss and Real Loss. Use volumes & values.
Prioritize the components to make a plan of attack.

## Slide 82
Component Analysis – Apparent Losses
82

## Slide 85
Volume
Value

## Slide 86
Volume
Value
Small Meter Inaccuracy
Large Meter Inaccuracy
Meter Mis-Application
Level 4
Level 4

## Slide 87
Component Analysis – Apparent Loss
87
Sample Testing for Small Meters

## Slide 88
Component Analysis – Apparent Loss
88
Sample Testing for Small Meters
  Select sample to test
    Statistical significance (confidence, margin of error)
    Consider resources for testing
    Sample each type of meter with designed flow rate boundaries
  Described in AWWA M6 Manual

## Slide 89
Chart: Count
| Small Meters | Large Meters
Count | 32000 | 1000
Chart: Volume (MG)
| Small Meters | Large Meters
Volume (MG) | 4523.75 | 5599
Component Analysis – Apparent Loss
Number of Meters in System
Revenue from Each Class of Meters
Notes: 89

## Slide 90
Component Analysis – Apparent Loss
90
Targeted testing for Large Meters
  Annual revenue from large meters = $100,000
  Estimated inaccuracy = 5 %
  Annual large meter revenue loss = $5,000

## Slide 91
Component Analysis – Apparent Loss
91
Picking which large meters to test
  Annual revenue from specific large meter = $10,000
  Estimated inaccuracy = 10%
  Annual large meter revenue being lost = $1,000
  Cost to test/repair meter = $ 500
  Is it worth it to test/repair this meter?

## Slide 92
Component Analysis – Apparent Loss
92
Picking which meters to test
  Annual revenue from specific meter = $6,000
  Estimated inaccuracy = 5%
  Annual large meter revenue loss = $300
  Cost to test/repair meter = $ 500
  Is it working it to test/repair this meter?

## Slide 93
Component Analysis – Apparent Loss
93
Picking which meters to test
  Annual revenue from specific meter = $25,000
  Estimated inaccuracy = 2%
  Annual large meter revenue loss = $500
  Cost to test/repair meter = $500
  Is it worth it to test/repair this meter?

## Slide 94
Toolbox
94
The Toolbox (Basic) | Helps to Address | Level of Cost
1 - Validation of supply & consumption volumes | Low Data Validity Score, Gremlins | Low-Mid
2 - Estimating and tracking unmetered use | Validity, Unmetered Use | None-Low
3 - Installing meters on unmetered connections | Unmetered Use | Mid
4 - Billing system audit | Systematic Data Handling Errors | Low-Mid
5 - Meter testing & replacement | Customer metering inaccuracy | Mid-High
6 - Unidirectional flushing program | Unbilled unmetered | Low
7 - Acoustic leak survey | Unreported leakage | Mid
8 - Improve speed/quality of repairs | Unreported, Reported leakage | Low
9 - Locate & eliminate pressure transients (surges, hammers) | All 3 types of leakage | Low-Mid
10 - Reduce peak and overall pressure | All 3 types of leakage | Mid-High

## Slide 95
Toolbox
95
Unreported
Reported
Background

## Slide 96
Toolbox
96
The Toolbox (Basic) | Helps to Address | Level of Cost
1 - Validation of supply & consumption volumes | Low Data Validity Score, Gremlins | Low-Mid
2 - Estimating and tracking unmetered use | Validity, Unmetered Use | 
3 - Installing meters on unmetered connections | Unmetered Use | Mid
4 - Billing system audit | Systematic Data Handling Errors | Low-Mid
5 - Meter testing & replacement | Customer metering inaccuracy | Mid-High
6 - Unidirectional flushing program | Unbilled unmetered | Low
7 - Acoustic leak survey | Unreported leakage | Mid
8 - Improve speed/quality of repairs | Unreported, Reported leakage | Low
9 - Locate & eliminate pressure transients (surges, hammers) | All 3 types of leakage | Low-Mid
10 - Reduce peak and overall pressure | All 3 types of leakage | Mid-High

## Slide 97
Toolbox
97
Unreported
Reported
Background

## Slide 98
Toolbox
98
The Toolbox (Basic) | Helps to Address | Level of Cost
1 - Validation of supply & consumption volumes | Low Data Validity Score, Gremlins | Low-Mid
2 - Estimating and tracking unmetered use | Validity, Unmetered Use | 
3 - Installing meters on unmetered connections | Unmetered Use | Mid
4 - Billing system audit | Systematic Data Handling Errors | Low-Mid
5 - Meter testing & replacement | Customer metering inaccuracy | Mid-High
6 - Unidirectional flushing program | Unbilled unmetered | Low
7 - Acoustic leak survey | Unreported leakage | Mid
8 - Improve speed/quality of repairs | Unreported, Reported leakage | Low
9 - Locate & eliminate pressure transients (surges, hammers) | All 3 types of leakage | Low-Mid
10 - Reduce peak and overall pressure | All 3 types of leakage | Mid-High

## Slide 99
Toolbox
99
Unreported
Reported
Background

## Slide 100
Toolbox
100
The Toolbox (Basic) | Helps to Address | Level of Cost
1 - Validation of supply & consumption volumes | Low Data Validity Score, Gremlins | Low-Mid
2 - Estimating and tracking unmetered use | Validity, Unmetered Use | 
3 - Installing meters on unmetered connections | Unmetered Use | Mid
4 - Billing system audit | Systematic Data Handling Errors | Low-Mid
5 - Meter testing & replacement | Customer metering inaccuracy | Mid-High
6 - Unidirectional flushing program | Unbilled unmetered | Low
7 - Acoustic leak survey | Unreported leakage | Mid
8 - Improve speed/quality of repairs | Unreported, Reported leakage | Low
9 - Locate & eliminate pressure transients (surges, hammers) | All 3 types of leakage | Low-Mid
10 - Reduce peak and overall pressure | All 3 types of leakage | Mid-High

## Slide 101
Toolbox – Data Validity
101
If Data Validity Score is less than 50, focus on improving data validity
  Validation of supply & consumption volumes
  Estimating and tracking unmetered use
  Master Meter annual testing program
  Mapping the water system

## Slide 102
Toolbox – Authorized, Unbilled usage
102
If Data Validity Score is greater than 50, and If areas of focus include Authorized, Unbilled consumption:
  Review policies & procedures for unbilled customers
  Install meters on unmetered connections
  Unidirectional Flushing Program
  Customer meter testing & replacement program
  Theft deterrence
  Billing system audit

## Slide 103
Toolbox: Real Losses
103
If Data Validity Score is greater than 50, and if areas of focus include real losses:
  Collecting & Analysis of break data
  Improve speed/quality of repairs
  Locate & eliminate pressure transients (surges, hammers, etc.)
  Night flow analysis
  Reduce peak & overall pressure
  Main replacement
  Acoustic Leak Survey

## Slide 104
Real Loss Component Analysis Results
104

## Slide 105
Real Loss Component Analysis Results
105

## Slide 106
Real Loss Component Analysis Results
106

## Slide 107
Real Loss Component Analysis Results
107

## Slide 108
Real Loss Component Analysis Results
108

## Slide 109
Summary and Toolbox Decisions – Activity 4
109
Placeholder for Hands-On Activity #4
  ID all appropriate toolbox tools to address NRW for each system in A#4 Toolbox Decision Exercise
  Fine-tune Rockville WSC audit for individual data validity, overall data score, performance indicators and total annual cost of NRW
    ID all appropriate toolbox tools to address Rockville WSC NRW
Applied Activity #4
  Summarize your own system’s audit
  ID all appropriate toolbox tools to address your NRW

## Slide 110
What we learned
110
What is a Water Audit?
What are the Benefits to annual water audits?
What triggers voluntary & required water audits?
How to conduct a water audit using AWWA M36 software
How to interpret and report data validity
How to interpret audit results – Volumes and Values
How to interpret results from AWWA M36 software
How to use results to implement corrective actions

## Slide 111
Hands-On Activity #1
111
Go to www.awwa.org to download a copy of the free water audit software to your computer
Open the software (enable editing, content, macros) to ensure it works – you need Excel
Use the Rockville Water Supply Corp Background Info to enter data into the software
  Use A#1 Software Exercise Results Excel file to check your entries for all software tabs
Use this water balance exercise to identify your own system data needed to populate audit inputs

## Slide 112
Hands-On Activity #2
112
Use the A#2 Data Validity Exercise to fine-tune the water balance inputs for the Rockville WSC
  Use the A#2 Data Validity Exercise Trainer Notes for the water balance breakdown
Input water balance data without, and then with data grades
  Download each audit separately to see how it displays validity data without and with data grades
  Compare your results with the A#2 Exercise Results without and with data grades

## Slide 113
Applied Activity #2
113
Follow the instructions presented in the A#2 Data Validity Applied Activity to assign data validity scores for each water balance component of your water system
This will identify those components of your water balance that need more attention in order to bring your overall data validity score > 50

## Slide 114
Hands-On Activity #3
114
Download a copy of the free AWWARf Leakage Component Analysis Model from http://www.waterrf.org/resources/pages/PublicWebTools-detail.aspx?ItemID=27 to your computer
Open the software (enable editing, content, macros) to ensure it works – you need Excel
Expand the Rockville water balance by following instructions and using data from the A#3a Real Loss and #3b Leakage Component Analysis exercises
  This will ID the real loss sub-component of NRW

## Slide 115
Applied Activity #3
115
Follow the instructions presented in the A#3 Real Loss and Leakage Component Applied Activity to assemble main and service line break and leakage data
If you already have this data for your water system enter it into the AWWARf Leakage Component Analysis Model
  Otherwise, develop a plan for your system to collect and maintain records of this data
This will allow you to use the software to calculate the real loss sub-components of your NRW

## Slide 116
Hands-On Activity #4
116
Use the A#4 Toolbox Decision Exercise to evaluate each of the systems audit results for overall validity score, performance indicators and total annual cost of NRW
On each systems evaluation form record your observations of the metrics, the top three focus areas and from the ten toolbox tools the best tool(s) to address each focus area
Check your conclusions using the A#4 Toolbox Decision Exercise Trainer Notes

## Slide 117
Applied Activity #4
117
Follow the instructions presented in the A#4 Summary and Toolbox Decision Applied Activity to work through an entire audit for your system
You may already have previous steps of the audit completed; use this activity to review the data you used for those steps
Develop a plan to continue to improve system data for the audit and create a schedule to conduct the audit annually

## Slide 118
Questions?
118
Thank you